## ERCPL Performance
[34 empty] | TL Loss% | 0.35%
| SECI-III | [8 empty] | AC Cap |  |  | 300 |  |  |  |  | SECI-III -Shortfall Analysis | [15 empty] | AC Loss% | 2%
Connected DC Capacity (MWp) | Months | Budget Gen (MWHr) | Pridiction Gen (MWHr) | Actual Gen (MWHr) | Budget GHI (KWHr/m2) | Actual GHI (KWHr/m2) | Budget GTI (KWHr/m2) | Actual GTI (KWHr/m2) | PR Budgeted(%) | PR Achieved(%) | CUF Budgeted (%) | CUF Achieved (%) | Budgeted Plant Av(%) | Actual Plant Av(%) | Budgeted Grid Av(%) | Actual Grid Av(%) |  | Months | Shortfall in Gen(%) wrt Budget | Shortfall in Gen(%) wrt Prediction | Shortfall in Rad(%) | Shortfall in Plant Av(%) | Shortfall in Grid Av(%) | Generation loss in Grid Compliance (%) | Shadow Loss | Grid Limitation 300MW | Avg Set Point PPC | Generation(MWh) Above 300MW | Generation(MWh) Above 300MW (%) | Less Degradation considered (2.5%-1.65%)=0.85% | Soil Loss(%) |  | Un Identified | Budgeted Inverter Gen. MWHr | Actual Inverter Gen. MWHr | Budgeted Monthly Module Temp (°C) | Actual Monthly Module Temp (°C) | Budgeted Temp Loss % | Actual Temp Loss % | Budgeted Inverter Clipping % | Actual Inverter Clipping % | Grid Limitation Loss %
309.2589 | 2021-08-31 | 25834.1598 | 29085.0786 | 26127.968 | 96.7355 | 114.724 | 97.4484 | 117.2813 | 86.15% | 74.13% | 21.11% | 21.35% | 99.5% | 97.17% | 100% | 99.45% | -19.21% | 2021-08-31 | 1.137% | -10.17% | 20.35% | -2.327% | -0.5526% | -1.45% | -0.2% | -2.275% | 325 | 0 |  | -0.85% |  | -17.56% | -17.24% | 26453.9764 | 10229.638 | 41.258
407.1342 | 2021-09-30 | 62482.4029 | 54887.3628 | 50430.016 | 181.1 | 160.6876 | 194.4 | 171.885 | 79.34% | 74.59% | 28.93% | 23.35% | 99.5% | 96.61% | 100% | 100% | -7.707% | 2021-09-30 | -19.29% | -8.121% | -11.58% | -2.889% | 0% | -3.209% | -0.2% | -3.508% | 325 | 0 |  | -0.85% |  | -4.298% | -3.409% | 63981.4892 | 51521.9234 | 44.311
426.3295 | 2021-10-31 | 68872.8453 | 68797.4608 | 62683.872 | 174.6 | 169.3538 | 204 | 200.6888 | 79.59% | 74.07% | 30.86% | 28.08% | 99.5% | 98.91% | 100% | 100% | -7.363% | 2021-10-31 | -8.986% | -8.886% | -1.623% | -0.5851% | 0% | -2.876% | -0.2% | -3.477% | 325 | 5.8 | 0.009221% | -0.85% | -6.585% | -4.287% | 0.8839% | 70525.2519 | 64248.352 | 44.072 | 39.8778
436.8501 | 2021-11-30 | 61392.2062 | 60335.7562 | 53646.08 | 135 | 132.217 | 168.9 | 168.0337 | 83.62% | 73.3% | 28.42% | 24.84% | 99.5% | 99.71% | 100% | 100% | -12.1% | 2021-11-30 | -12.62% | -11.09% | -0.5129% | 0.2062% | 0% | -0.5276% | -0.2% | -2.787% | 325 | 0.7 | 0.0013% | -0.85% | -8.654% | -11.38% | -4.929% | 62865.1364 | 54795.926 | 38.536 | 33.6791
444.9055 | 2021-12-31 | 61807.1225 | 53948.589 | 51885.6 | 124.1 | 114.5987 | 162.6 | 146.8345 | 85.87% | 79.95% | 27.69% | 23.25% | 99.5% | 99.34% | 100% | 100% | -6.357% | 2021-12-31 | -16.05% | -3.824% | -9.696% | -0.1591% | 0% | -2.316% | -0.2% | -2.355% | 325 | 161.5 | 0.3102% | -0.85% | -5.65% | -3.84% | -0.03134% | 63290.0074 | 53050.149 | 30.842 | 26.1537
445.4393 | 2022-01-31 | 64420.8756 | 58590.7279 | 57593.376 | 132.8 | 126.5179 | 170.1 | 160.5455 | 85.45% | 81.09% | 28.86% | 25.8% | 99.5% | 99.31% | 100% | 99.9% | -4.981% | 2022-01-31 | -10.6% | -1.702% | -5.617% | -0.1892% | -0.09692% | -2.847% | -0.2% | -4.168% | 325 | 542.3 | 0.9383% | -0.85% | -2.17% | -1.935% | -1.575% | 65966.47 | 58948.923 | 29.262 | 26.1772 | 3.364% |  | 0.8766%
445.4393 | 2022-02-28 | 63303.9812 | 64981.0186 | 61555.36 | 144.8 | 150.7646 | 174 | 180.9115 | 82.09% | 76.79% | 31.4% | 30.53% | 99.5% | 99.47% | 100% | 99.63% | -6.734% | 2022-02-28 | -2.762% | -5.272% | 3.972% | -0.02654% | -0.3736% | -3.131% | -0.2% | -4.933% | 325 | 384.4 | 0.6223% | -0.85% | -2.483% | -3.404% | -2.894% | 64822.7789 | 63093.549 | 36.494 | 33.1502 | 6.006% |  | 2.524%
445.4393 | 2022-03-31 | 75049.1013 | 78128.9161 | 71367.744 | 194.7 | 201.2519 | 216.1 | 222.3009 | 78.36% | 72.12% | 33.62% | 31.97% | 99.5% | 99.93% | 100% | 100% | -7.775% | 2022-03-31 | -4.905% | -8.654% | 2.869% | 0.429% | 0% | -2.901% | -0.2% | -4.428% | 325 | 400.9 | 0.5598% | -0.85% | -3.03% | -4.674% | -4.073% | 76849.6895 | 73222.3265 | 42.611 | 41.2326 | 8.553% |  | 4.682%
445.638 | 2022-04-30 | 73220.2639 | 77639.3481 | 72238.848 | 209.6 | 220.8757 | 215.9 | 227.0443 | 76.48% | 71.49% | 33.9% | 33.44% | 99.5% | 99.87% | 100% | 100% | -6.502% | 2022-04-30 | -1.34% | -6.956% | 5.162% | 0.3718% | 0% | -3.184% | -0.2% | -2.998% | 325 | 220.2 | 0.3038% | -0.85% | -2.14% | -3.118% | -3.35% | 74976.9744 | 74204.4271 | 48.508 | 48.145 | 10.64% | -11.62% | 4.495% | -5.685%
446.413 | 2022-05-31 | 75517.4708 | 79062.9748 | 72090.208 | 221.5 | 229.8106 | 217.1 | 224.6078 | 78.31% | 71.96% | 33.83% | 32.3% | 99.5% | 99.91% | 100% | 100% | -7.997% | 2022-05-31 | -4.538% | -8.819% | 3.458% | 0.4147% | 0% | -3.439% | -0.2% | -2.268% | 325 | 39.6 | 0.05474% | -0.85% | -2.93% | -4.357% | -3.842% | 77329.2962 | 73965.8354 | 47.724 | 46.6374 | 10.48% | -11.28% | 2.045% | -2.996%
446.5031 | 2022-06-30 | 67324.104 | 72923.2944 | 67445.248 | 198.6 | 213.1332 | 190.5 | 203.2221 | 79.55% | 74.46% | 31.17% | 31.22% | 99.5% | 99.83% | 100% | 100% | -6.498% | 2022-06-30 | 0.1799% | -7.512% | 6.678% | 0.3271% | 0% | -2.537% | -0.2% | -1.799% | 325 | 171.6 | 0.2535% | -0.85% | -2.04% | -3.761% | -4.048% | 68939.353 | 69087.6741 | 45.695 | 43.9548 | 9.714% | -10.16% | 0.9112% | -1.78%
447.0515 | 2022-07-31 | 61732.76 | 57594.6828 | 54100.224 | 177 | 162.85 | 171.5 | 157.32 | 80.92% | 77.19% | 27.66% | 24.24% | 99.5% | 99.65% | 100% | 100% | -4.096% | 2022-07-31 | -12.36% | -6.067% | -8.268% | 0.15% | 0% | -2.167% | -0.2% | -1.467% | 325 | 57.7 | 0.1063% | -0.85% | -0.36% | -1.729% | -3.519% | 63213.8608 | 55303.1676 | 42.219 | 38.3832 | 8.382% | -7.779% | 0.4348% | -0.7806%
447.9628 | 2022-08-31 | 64124.8528 | 56571.7486 | 53422.944 | 176.4 | 155.0984 | 177.7 | 154.7145 | 80.96% | 77.65% | 28.73% | 23.94% | 99.5% | 99.27% | 100% | 99.92% | -3.754% | 2022-08-31 | -16.69% | -5.566% | -12.93% | -0.2319% | -0.08% | -2.507% | -0.2% | -2.275% | 325 | 10.826 | 0.02019% | -0.85% | -0.46% | -1.047% | -2.355% | 65663.345 | 54596.6028 | 41.258 | 37.7274 | 8.003% | -7.005% | 1.061% | -0.4065%
448.3171 | 2022-09-30 | 68458.6739 | 72306.92 | 67125.728 | 181.1 | 188.8552 | 194.4 | 202.4372 | 78.94% | 74.1% | 31.69% | 31.08% | 99.5% | 99.81% | 100% | 100% | -6.081% | 2022-09-30 | -1.947% | -7.166% | 4.134% | 0.3129% | 0% | -2.865% | -0.2% | -3.508% | 324.5 | 123.6 | 0.1835% | -0.85% | -1.56% | -3.016% | -3.769% | 70101.1437 | 68787.8152 | 44.311 | 43.3355 | 8.938% | -8.752% | 2.605% | -3.393%
448.3345 | 2022-10-31 | 72065.4975 | 72885.1097 | 69307.328 | 174.6 | 175.2819 | 204 | 203.8132 | 79.19% | 76.02% | 32.29% | 31.05% | 99.5% | 99.77% | 100% | 100% | -3.736% | 2022-10-31 | -3.827% | -4.909% | -0.09159% | 0.2734% | 0% | -1.686% | -0.2% | -3.477% | 310.8387 | 795.1 | 1.143% | -0.85% | -2.44% | -1.85% | -1.683% | 73794.5027 | 70950.6459 | 44.072 | 41.6818 | 8.846% | -9.37% | 2.625% | -3.04%
448.3467 | 2022-11-30 | 62692.8219 | 64515.9141 | 60799.008 | 135 | 137.1418 | 168.9 | 171.9937 | 83.21% | 78.9% | 29.02% | 28.15% | 99.5% | 99.93% | 100% | 100% | -4.852% | 2022-11-30 | -3.021% | -5.761% | 1.832% | 0.4276% | 0% | -1.686% | -0.2% | -2.787% | 310 | 476.1 | 0.7803% | -0.85% | -2.32% | -2.967% | -3.074% | 64196.9566 | 62140.2596 | 38.536 | 35.9685 | 6.583% | -7.24% | 0.4933% | -0.8%
448.3467 | 2022-12-31 | 61973.7454 | 66618.8903 | 60948.16 | 124.1 | 130.5268 | 162.6 | 171.8058 | 85.44% | 80.18% | 27.77% | 27.31% | 99.5% | 98.68% | 100% | 100% | -7.316% | 2022-12-31 | -1.655% | -8.512% | 5.662% | -0.8153% | 0% | -3.11% | -0.2% | -2.355% | 310 | 408 | 0.6671% | -0.85% | -2.48% | -4.006% | -2.711% | 63460.6279 | 62329.4327 | 30.842 | 29.928 | 3.753% |  | 0.01658%
448.3467 | 2023-01-31 | 64517.1458 | 66977.0334 | 63197.28 | 132.8 | 137.3141 | 170.1 | 174.3934 | 85.02% | 81.51% | 28.91% | 28.31% | 99.5% | 99.16% | 100% | 99.63% | -4.57% | 2023-01-31 | -2.046% | -5.643% | 2.524% | -0.3372% | -0.3667% | -2.448% | -0.2% | -4.168% | 309.1935 | 646.2 | 1.019% | -0.85% | -2.31% | -1.922% | -1.274% | 66065.0499 | 64522.168 | 29.262 | 25.7023 | 3.364% |  | 0.8766%
448.3467 | 2023-02-28 | 63398.5823 | 63763.0455 | 59671.04 | 144.8 | 150.4873 | 174 | 180.1725 | 81.68% | 76.25% | 31.45% | 29.6% | 99.5% | 96.88% | 100% | 99.29% | -9.427% | 2023-02-28 | -5.88% | -6.418% | 3.547% | -2.622% | -0.7111% | -1.924% | -0.2% | -4.933% | 304.8571 | 285.1 | 0.4761% | -0.85% | -2.13% | -7.303% | -4.552% | 64919.6497 | 61038.242 | 36.494 | 36.4905 | 6.006% |  | 2.524%
448.3467 | 2023-03-31 | 75161.2542 | 70741.6544 | 67980.672 | 194.7 | 184.0646 | 216.1 | 202.3952 | 77.97% | 75.02% | 33.67% | 30.46% | 99.5% | 99.86% | 100% | 100% | -3.212% | 2023-03-31 | -9.554% | -3.903% | -6.342% | 0.3602% | 0% | -0.1259% | -0.2% | -4.428% | 303 | 258 | 0.3782% | -0.85% | -1.456% | -2.886% | -3.79% | 76964.5332 | 69402.6799 | 42.611 | 37.6069 | 8.553% |  | 4.682%
448.3467 | 2023-04-30 | 72929.5305 | 71738.6609 | 68328.128 | 209.6 | 205.3056 | 215.9 | 209.5863 | 75.72% | 72.82% | 33.76% | 31.63% | 99.5% | 99.85% | 100% | 100% | -3.385% | 2023-04-30 | -6.309% | -4.754% | -2.924% | 0.3541% | 0% | -0.151% | -0.2% | -2.998% | 303 | 239.3 | 0.349% | -0.85% | -2% | -3.034%
448.3467 | 2023-05-31 | 75089.195 | 77534.0789 | 71408.672 | 221.5 | 228.1174 | 217.1 | 220.7134 | 77.53% | 73.45% | 33.64% | 31.99% | 99.5% | 98.25% | 100% | 100% | -6.566% | 2023-05-31 | -4.902% | -7.9% | 1.664% | -1.254% | 0% | -1.714% | -0.2% | -2.268% | 305.7097 | 468.3 | 0.6535% | -0.85% | -1.771% | -4.652%
448.3467 | 2023-06-30 | 67263.1714 | 69737.4535 | 66229.888 | 198.6 | 207.1279 | 190.5 | 196.037 | 79.15% | 76% | 31.14% | 30.66% | 99.5% | 99.15% | 100% | 100% | -4.443% | 2023-06-30 | -1.536% | -5.03% | 2.907% | -0.3467% | 0% | -3.56% | -0.2% | -1.799% | 303.0667 | 168.2 | 0.2531% | -0.85% | -1.531% | -0.6831%
448.3467 | 2023-07-31 | 61601.2288 | 68246.2219 | 64062.976 | 177 | 195.3266 | 171.5 | 186.7982 | 80.52% | 76.82% | 27.6% | 28.7% | 99.5% | 99.57% | 100% | 100% | -4.924% | 2023-07-31 | 3.996% | -6.13% | 8.92% | 0.07316% | 0% | -3.461% | -0.2% | -1.467% | 305 | 148.3 | 0.2307% | -0.85% | -0.6995% | -1.263%
448.3467 | 2023-08-31 | 63858.0561 | 71188.2081 | 65427.904 | 176.4 | 196.4225 | 177.7 | 196.0407 | 80.55% | 74.65% | 28.61% | 29.31% | 99.5% | 99.72% | 100% | 100% | -7.863% | 2023-08-31 | 2.458% | -8.092% | 10.32% | 0.2241% | 0% | -3.588% | -0.2% | -2.275% | 305 | 165.3 | 0.2518% | -0.85% | -1.764% | -4.075%
448.3467 | 2023-09-30 | 68119.9708 | 68032.3771 | 63012.256 | 181.1 | 179.3213 | 194.4 | 191.2213 | 78.55% | 73.75% | 31.54% | 29.17% | 99.5% | 99.66% | 100% | 100% | -5.863% | 2023-09-30 | -7.498% | -7.379% | -1.635% | 0.1592% | 0% | -3.181% | -0.2% | -3.508% | 305 | 242.6 | 0.3837% | -0.85% | -1.44% | -2.482%
448.3467 | 2023-10-31 | 71706.1622 | 67790.909 | 64901.76 | 174.6 | 163.7386 | 204 | 191.6879 | 78.79% | 75.9% | 32.13% | 29.08% | 99.5% | 99.49% | 100% | 100% | -3.454% | 2023-10-31 | -9.489% | -4.262% | -6.035% | -0.00777% | 0% | -2.742% | -0.2% | -3.477% | 305 | 362.2 | 0.5561% | -0.85% | -1.364% | -0.5124%
448.3467 | 2023-11-30 | 62378.5313 | 53551.718 | 51211.072 | 135 | 116.676 | 168.9 | 144.3449 | 82.79% | 79.22% | 28.88% | 23.71% | 99.5% | 99.89% | 100% | 100% | -3.364% | 2023-11-30 | -17.9% | -4.371% | -14.54% | 0.3929% | 0% | -0.8003% | -0.2% | -2.787% | 305 | 100 | 0.1946% | -0.85% | -1.431% | -2.364%
448.3467 | 2023-12-31 | 61663.0597 | 63643.0643 | 59413.376 | 124.1 | 124.3882 | 162.6 | 165.7518 | 85.01% | 80.06% | 27.63% | 26.62% | 99.5% | 99.86% | 100% | 100% | -5.587% | 2023-12-31 | -3.648% | -6.646% | 1.938% | 0.3573% | 0% | -0.058% | -0.2% | -2.355% | 305 | 197.1 | 0.3306% | -0.85% | -1.748% | -5.329%
448.3467 | 2024-01-31 | 64193.7095 | 62434.5071 | 58941.92 | 132.8 | 127.4055 | 170.1 | 164.2149 | 84.6% | 80.97% | 28.76% | 26.41% | 99.5% | 98.87% | 100% | 100% | -4.721% | 2024-01-31 | -8.181% | -5.594% | -3.46% | -0.6303% | 0% | -0.08% | -0.2% | -4.168% | 305 | 322 | 0.5444% | -0.85% | -1.62% | -4.441% | -4.191% | 65733.8537 | 64522.168 | 29.262 | 25.7023 | 3.364% |  | 0.8766%
448.3467 | 2024-02-29 | 63080.7536 | 64040.2185 | 60460.608 | 144.8 | 145.494 | 174 | 175.2304 | 81.27% | 77.13% | 31.29% | 29.99% | 99.5% | 99.78% | 100% | 100% | -4.861% | 2024-02-29 | -4.154% |  | 0.7071% | 0.2773% | 0% | -0.1195% | -0.2% | -4.933% | 305 |  |  | -0.85% | -1.55% | -4.541% | -5.269% | 64594.1956 | 61038.242 | 36.494 | 36.4905 | 6.006% |  | 2.524%
448.3467 | 2024-03-31 | 74784.457 | 75094.0052 | 71643.94 | 194.7 | 194.4917 | 216.1 | 215.8082 | 77.57% | 74.08% | 33.51% | 32.1% | 99.5% | 99.95% | 100% | 100% | -4.064% | 2024-03-31 | -4.199% |  | -0.135% | 0.4544% | 0% | -0.0929% | -0.2% | -4.428% | 305 |  |  | -0.85% | -1.99% | -3.772% | -4.236% | 76578.6959 | 69402.6799 | 42.611 | 37.6069 | 8.553% |  | 4.682%
448.3467 | 2024-04-30 | 72564.8828 | 67004.8046 | 65689.28 | 209.6 | 191.2995 | 215.9 | 196.8218 | 75.34% | 74.73% | 33.59% | 30.41% | 99.5% | 99.61% | 100% | 100% | -0.6385% | 2024-04-30 | -9.475% |  | -8.837% | 0.1123% | 0% | -0.1812% | -0.2% |  | 305 |  |  | -0.85% | -1.58% | -0.2573%
448.3467 | 2024-05-31 | 74713.749 | 78152.1782 | 72652.704 | 221.5 | 228 | 217.1 | 223.25 | 77.14% | 72.68% | 33.47% | 32.55% | 99.5% | 99.87% | 100% | 100% | -5.591% | 2024-05-31 | -2.759% |  | 2.833% | 0.37% | 0% | -0.2% | -0.2% |  | 305 |  |  | -0.85% | -2.25% | -5.191%
448.3467 | 2024-06-30 | 66926.8555 | 71102.3382 | 66712.544 | 198.6 | 208.2414 | 190.5 | 199.1303 | 78.75% | 74.85% | 30.98% | 30.89% | 99.5% | 99.83% | 100% | 100% | -4.851% | 2024-06-30 | -0.3202% |  | 4.53% | 0.3259% | 0% | -0.5286% | -0.2% |  | 305 |  |  | -0.85% | -1.71% | -4.122%
448.3467 | 2024-07-31 | 61293.2226 | 70631.3206 | 65727.552 | 177 | 199.1783 | 171.5 | 194.2427 | 80.11% | 75.99% | 27.46% | 29.45% | 99.5% | 99.32% | 100% | 100% | -6.026% | 2024-07-31 | 7.235% |  | 13.26% | -0.18% | 0% | -0.3315% | -0.2% |  | 303 |  |  | -0.85% | -0.79% | -5.495%
448.3467 | 2024-08-31 | 63538.7658 | 53075.9836 | 50124.128 | 176.4 | 145.5852 | 177.7 | 146.4989 | 80.15% | 77.71% | 28.47% | 22.46% | 99.5% | 98.2% | 100% | 100% | -3.554% | 2024-08-31 | -21.11% |  | -17.56% | -1.3% | 0% | -0.2186% | -0.2% |  | 303 |  |  | -0.85% | -0.25% | -3.136%
448.3467 | 2024-09-30 | 67779.3709 |  | 63393.888 | 181.1 | 175.7966 | 194.4 | 191.32 | 78.16% | 74.67% | 31.38% | 29.35% | 99.5% | 98.97% | 100% | 100% | -4.886% | 2024-09-30 | -6.47% |  | -1.584% | -0.53% | 0% | -0.1976% | -0.2% |  | 303 |  |  | -0.85% | -1.08% | -4.488%
448.3467 | 2024-10-31 | 71347.6314 |  | 64137.792 | 174.6 | 163.23 | 204 | 192.98 | 78.4% | 74.31% | 31.97% | 28.74% | 99.5% | 99.76% | 100% | 100% | -4.703% | 2024-10-31 | -10.11% |  | -5.402% | 0.26% | 0% | -0.491% | -0.2% |  | 303 |  |  | -0.85% | -1.08% | -4.012%
448.3467 | 2024-11-30 | 62066.6387 |  | 58676.064 | 135 | 133.2662 | 168.9 | 172.0071 | 82.37% | 76.14% | 28.73% | 27.16% | 99.5% | 99.93% | 100% | 100% | -7.302% | 2024-11-30 | -5.463% |  | 1.84% | 0.43% | 0% | -0.6963% | -0.2% |  | 303 |  |  | -0.85% | -2.13% | -6.406%
448.3467 | 2024-12-31 | 61354.7444 |  | 56765.984 | 124.1 | 122.0631 | 162.6 | 162.536 | 84.58% | 78.21% | 27.49% | 25.43% | 99.5% | 99.6% | 100% | 100% | -7.44% | 2024-12-31 | -7.479% |  | -0.03936% | 0.1% | 0% | -0.6946% | -0.2% |  | 303 |  |  | -0.85% | -2.17% | -6.545%
448.3467 | 2025-01-31 | 63872.741 |  | 61904.06 | 132.8 | 133.16 | 170.1 | 174.86 | 84.17% | 80.04% | 28.62% | 27.73% | 99.5% | 98.65% | 100% | 100% | -5.881% | 2025-01-31 | -3.082% |  | 2.798% | -0.85% | 0% | -0.9524% | -0.2% |  | 303 |  |  | -0.85% | -1.95% | -4.728%
448.3467 | 2025-02-28 | 62765.3498 |  | 57634.88 | 144.8 | 137.78 | 174 | 167.29 | 80.86% | 76.98% | 31.13% | 28.59% | 99.5% | 99.82% | 100% | 100% | -4.318% | 2025-02-28 | -8.174% |  | -3.856% | 0.32% | 0% | -1.338% | -0.2% |  | 303 |  |  | -0.85% | -1.95% | -2.779%
448.3467 | 2025-03-31 | 74684.9322
448.3467 | 2025-04-30 | 72832.4742
448.3467 | 2025-05-31 | 74989.2646
448.3467 | 2025-06-30 | 66837.7877
448.3467 | 2025-07-31 | 61211.6522
448.3467 | 2025-08-31 | 63454.207
448.3467 | 2025-09-30 | 67689.1686
448.3467 | 2025-10-31 | 71252.6803
448.3467 | 2025-11-30 | 61984.039
448.3467 | 2025-12-31 | 61273.0921
| CY-21 | 280388.7367 | 267054.2474 | 244773.536 | 711.5355 | 691.5811 | 827.3484 | 804.7233 | 82.91% | 75.21% | 27.4% | 24.17% | 99.5% | 98.35% | 100% | 99.89% | -9.967% | CY-21 | -12.7% | -8.343% | -2.735% | -1.151% | -0.1105% | -2.076% | -0.2% | -2.88% | 325 | 168 | 0.06863% | -0.85% | -6.963% | -2.879% | -1.577% | 287115.8613 | 233845.9884 | 199.019 | 99.7106 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
| CY_22 | 809884.1484 | 821819.5454 | 767994.176 | 2070.2 | 2092.1081 | 2262.8 | 2280.7166 | 80.74% | 76% | 30.83% | 29.25% | 99.5% | 99.62% | 100% | 99.95% | -5.964% | CY_22 | -5.172% | -6.55% | 0.7918% | 0.1203% | -0.04587% | -2.672% | -0.2% | -3.039% | 321.2782 | 3630.326 | 0.4727% | -0.85% | -2.034% | 0.2031% | -3.178% | 829314.9988 | 786630.659 | 491.532 | 466.3217 | 7.772% | -9.151% | 1.897% | -2.36% | #DIV/0!
| CY_23 | 807685.8879 | 812944.4248 | 764845.024 | 2070.2 | 2088.29 | 2262.8 | 2259.1426 | 80.27% | 76.29% | 30.75% | 29.1% | 99.5% | 99.28% | 100% | 99.91% | -5.143% | CY_23 | -5.304% | -5.917% | -0.1616% | -0.2205% | -0.08981% | -1.979% | -0.2% | -3.039% | 304.9023 | 3280.6 | 0.4289% | -0.85% | -1.637% | 0.717% | -3.106% | 207949.2327 | 194963.0899 | 108.367 | 99.7997 | 5.974% | #DIV/0! | 2.694% | #DIV/0! | #DIV/0!
| CY_24 | 803644.7813 | 541535.3558 | 754926.404 | 2070.2 | 2034.0516 | 2262.8 | 2234.0402 | 79.87% | 75.96% | 30.59% | 28.74% | 99.5% | 99.47% | 100% | 100% | -4.791% | CY_24 | -6.062% | 39.4% | -1.271% | -0.02586% | 0% | -0.3193% | -0.2% | -4.51% | 304 | 322 | 0.04265% | -0.85% | -1.517% | 1.071% | -4.729% | 141884.1828 | 130440.9219 | 79.105 | 74.0974 | 7.28% | #DIV/0! | 3.603% | #DIV/0! | #DIV/0!
| CY_25 | 126638.0907 | 0 | 119538.94 | 277.6 | 270.94 | 344.1 | 342.15 | 82.52% | 78.51% | 29.88% | 28.16% | 99.5% | 99.24% | 100% | 100% | -5.039% | CY_25 | -5.606% | #DIV/0! | -0.5667% | -0.265% | 0% | -0.9524% | -0.2% | #DIV/0! | 303 | 0 | 0% | -0.85% | -1.95% | #DIV/0! | -3.672% | 76964.5332 | 69402.6799 | 42.611 | 37.6069 | 8.553% | #DIV/0! | 4.682% | #DIV/0! | #DIV/0!
| FY21-22 | 483162.6948 | 468754.91 | 435290.016 | 1183.8355 | 1170.1156 | 1387.5484 | 1368.4812 | 82.56% | 75.76% | 28.86% | 26.15% | 99.5% | 98.81% | 100% | 99.87% | -8.534% | FY21-22 | -9.908% | -7.139% | -1.374% | -0.6927% | -0.1279% | -2.407% | -0.2% | [5 empty] | -4.762% |  | -2.472% | 207949.2327 | 194963.0899 | 108.367 | 99.7997 | 5.974% | #DIV/0! | 2.694% | #DIV/0! | #DIV/0!
| FY22-23 | 810187.1725 | 821600.616 | 768326.688 | 2070.2 | 2085.4397 | 2262.8 | 2273.9197 | 80.64% | 76.23% | 30.84% | 29.26% | 99.5% | 99.39% | 100% | 99.9% | -5.658% | FY22-23 | -5.167% | -6.484% | 0.4914% | -0.114% | -0.09648% | -2.307% | -0.2% | [5 empty] | -1.886% |  | -3.152% | 141884.1828 | 130440.9219 | 79.105 | 74.0974 | 7.28% | #DIV/0! | 3.603% | #DIV/0! | #DIV/0!
| FY23-24 | 806667.8258 | 813031.4223 | 765042.5 | 2070.2 | 2083.8152 | 2262.8 | 2257.435 | 80.17% | 76.24% | 30.71% | 29.11% | 99.5% | 99.5% | 100% | 100% | -4.923% | FY23-24 | -5.16% | -5.902% | -0.2371% | 0.004516% | 0% | -1.629% | -0.2% | [5 empty] | -1.576% |  | -3.523% | 76964.5332 | 69402.6799 | 42.611 | 37.6069 | 8.553% | #DIV/0! | 4.682% | #DIV/0! | #DIV/0!
| FY24-25 | 728223.9519 | 339966.6251 | 683418.876 | 1875.5 | 1837.6004 | 2046.7 | 2020.9367 | 80% | 76.03% | 30.3% | 28.43% | 99.5% | 99.41% | 100% | 100% | -4.894% | FY24-25 | -6.153% | 101% | -1.259% | -0.08561% | 0% | -0.53% | -0.2% | [5 empty] | -1.54% |  | -4.538% | 0 | 0 | 0 | 0 | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
Formulas:
Months = [Months]
Months = EOMONTH([Months, row above],1)
Note on O4: Author: Plant Uptime-97.7127272727273%
Note on O22: Author: TL Down for 7 Hours considered in PU 97.63% TL Av.
Note on O25: Author: 98.87% TL Loss
Note on E46: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Standby Meter Readings

## Grid Compliance
Months | Active Energy (MWH) | Apparent Energy (MVAH) | Generation loss in Grid Compliance (MWH) | Generation loss in Grid Compliance (%) | Revenue loss in Grid Compliance (INR) | Remarks
2021-08-01 | 24135.03 | 24,490.48* | 355.45 | -1.45% | 924165 | Reading taken from TVM Energy Meter installed at our Plant end
2021-09-01 | 50839.25 | 52524.89 | 1685.64 | -3.209% | 4382664 | Reading taken from TVM Energy Meter installed at our Plant end
2021-10-01 | 63284.8 | 65159 | 1874.2 | -2.876% | 4872920 | Reading taken from TVM Energy Meter installed at our Plant end
2021-11-01 | 54125.5 | 54412 | 287.1 | -0.5276% | 746460 | Reading taken from TVM Energy Meter installed at our Plant end
2021-12-01 | 52353.3 | 53594.6 | 1241.3 | -2.316% | 3227380 | Reading taken from TVM Energy Meter installed at our Plant end
2022-01-01 | 58193.6 | 59898.7 | 1705.1 | -2.847% | 4433260 | Reading taken from TVM Energy Meter installed at our Plant end
2022-02-01 | 62097.2 | 64104 | 2006.8 | -3.131% | 5217680 | Reading taken from TVM Energy Meter installed at our Plant end
2022-03-01 | 72042.2 | 74194.4 | 2152.2 | -2.901% | 5595720 | Reading taken from TVM Energy Meter installed at our Plant end
Total | 437070.88 | 423887.59 | 11307.79 | -2.668% | 29400254
2022-04-01 | 72957.7 | 75357.2 | 2399.5 | -3.184% | 6238700 | Reading taken from TVM Energy Meter installed at our Plant end
2022-05-01 | 72790.8 | 75383.5 | 2592.7 | -3.439% | 6741020 | Reading taken from TVM Energy Meter installed at our Plant end
2022-06-01 | 68078.5 | 69850.6 | 1772.1 | -2.537% | 4607460 | Reading taken from TVM Energy Meter installed at our Plant end
2022-07-01 | 54605.2 | 55814.6 | 1209.4 | -2.167% | 3144440 | Reading taken from TVM Energy Meter installed at our Plant end
2022-08-01 | 53936.3 | 55323.2 | 1386.9 | -2.507% | 3605940 | Reading taken from TVM Energy Meter installed at our Plant end
2022-09-01 | 67755.8 | 69754.5 | 1998.7 | -2.865% | 5196620 | Reading taken from TVM Energy Meter installed at our Plant end
2022-10-01 | 69931.6 | 71130.8 | 1199.2 | -1.686% | 3117920 | Reading taken from TVM Energy Meter installed at our Plant end
2022-11-01 | 61356.8 | 62412.8 | 1056 | -1.692% | 2745600 | Reading taken from TVM Energy Meter installed at our Plant end
2022-12-01 | 61509.4 | 63483 | 1973.6 | -3.109% | 5131360 | Reading taken from TVM Energy Meter installed at our Plant end
2023-01-01 | 63753 | 65353 | 1600 | -2.448% | 4160000 | Reading taken from TVM Energy Meter installed at our Plant end
2023-02-01 | 60222.3 | 61403.5 | 1181.2 | -1.924% | 3071120 | Reading taken from TVM Energy Meter installed at our Plant end
2023-03-01 | 68599.7 | 68686.2 | 86.5 | -0.1259% | 224900 | Reading taken from TVM Energy Meter installed at our Plant end
Total | 775497.1 | 793952.9 | 18455.8 | -2.325% | 47985080
2023-04-01 | 68945.9 | 69050.2 | 104.3 | -0.151% | 271180 | Reading taken from TVM Energy Meter installed at our Plant end
2023-05-01 | 72061.4 | 73317.9 | 1256.5 | -1.714% | 3266900 | Reading taken from TVM Energy Meter installed at our Plant end
2023-06-01 | 66838.6 | 69305.6 | 2467 | -3.56% | 6414200 | Reading taken from TVM Energy Meter installed at our Plant end
2023-07-01 | 64668 | 66986.1 | 2318.1 | -3.461% | 6027060 | Reading taken from TVM Energy Meter installed at our Plant end
2023-08-01 | 66025.9 | 68483.2 | 2457.3 | -3.588% | 6388980 | Reading taken from TVM Energy Meter installed at our Plant end
2023-09-01 | 63633.5 | 65724.5 | 2091 | -3.181% | 5436600 | Reading taken from TVM Energy Meter installed at our Plant end
2023-10-01 | 65515.2 | 67362 | 1846.8 | -2.742% | 4801680 | Reading taken from TVM Energy Meter installed at our Plant end
2023-11-01 | 51702.9 | 52120 | 417.1 | -0.8003% | 1084460 | Reading taken from TVM Energy Meter installed at our Plant end
2023-12-01 | 59962.7 | 59997.5 | 34.8 | -0.058% | 90480 | Reading taken from TVM Energy Meter installed at our Plant end
2024-01-01 | 59477.4 | 59526 | 48.6 | -0.08164% | 126360 | Reading taken from TVM Energy Meter installed at our Plant end
2024-02-01 | 61009.9 | 61082.9 | 73 | -0.1195% | 189800 | Reading taken from TVM Energy Meter installed at our Plant end
2024-03-01 | 72269.8 | 72337 | 67.2 | -0.0929% | 174720 | Reading taken from TVM Energy Meter installed at our Plant end
Total | 772111.2 | 785292.9 | 13181.7 | -1.679% | 34272420
2024-04-01 | 66266.6 | 66386.9 | 120.3 | -0.1812% | 312780 | Reading taken from TVM Energy Meter installed at our Plant end
2024-05-01 | 73273.4 | 73416.9 | 143.5 | -0.1955% | 373100 | Reading taken from TVM Energy Meter installed at our Plant end
2024-06-01 | 67329.3 | 67687.1 | 357.8 | -0.5286% | 930280 | Reading taken from TVM Energy Meter installed at our Plant end
2024-07-01 | 66354.7 | 66575.4 | 220.7 | -0.3315% | 573820 | Reading taken from TVM Energy Meter installed at our Plant end
2024-08-01 | 50631.3 | 50742.2 | 110.9 | -0.2186% | 288340 | Reading taken from TVM Energy Meter installed at our Plant end
2024-09-01 | 64037.8 | 64164.6 | 126.8 | -0.1976% | 329680 | Reading taken from TVM Energy Meter installed at our Plant end
2024-10-01 | 64789.7 | 65109.4 | 319.7 | -0.491% | 831220 | Reading taken from TVM Energy Meter installed at our Plant end
2024-11-01 | 59254.3 | 59669.8 | 415.5 | -0.6963% | 1080300 | Reading taken from TVM Energy Meter installed at our Plant end
2024-12-01 | 57297.7 | 57698.5 | 400.8 | -0.6946% | 1042080 | Reading taken from TVM Energy Meter installed at our Plant end
2025-01-01 | 62463.4 | 63064 | 600.6 | -0.9524% | 1561560 | Reading taken from TVM Energy Meter installed at our Plant end
2025-02-01 | 57769.5 | 58553.2 | 783.7 | -1.338% | 2037620 | Reading taken from TVM Energy Meter installed at our Plant end
2025-03-01 |  |  | 0 | #DIV/0! | 0 | Reading taken from TVM Energy Meter installed at our Plant end
Total | 689467.7 | 693068 | 3600.3 | -0.5195% | 9360780

## Data
Plant | SPV | AC Capacity (MW) | Connected DC Capacity (MWp) | Months | Budget Gen (MWHr) | Actual Gen (MWHr) | Budget GHI (KWHr/m2) | Actual GHI (KWHr/m2) | Budget GTI (KWHr/m2) | Actual GTI (KWHr/m2) | PR Budgeted (%) | PR Achieved (%) | CUF Budgeted (%) | CUF Achieved (%) | Budgeted Plant Av (%) | Actual Plant Av (%) | Budgeted Grid Av (%) | Actual Grid Av (%) | Generation loss in Grid Compliance (%) | Soil Loss(%)
SECI-III | ERCPL | 300 | 309.2589 | 2021-08-31 | 25834.1598 | 26127.968 | 96.7355 | 114.724 | 97.4484 | 117.2813 | 86.15% | 74.13% | 21.11% | 21.35% | 99.5% | 97.17% | 100% | 99.45% | -1.45% | 0%
SECI-III | ERCPL | 300 | 407.1342 | 2021-09-30 | 62482.4029 | 50430.016 | 181.1 | 160.6876 | 194.4 | 171.885 | 79.34% | 74.59% | 28.93% | 23.35% | 99.5% | 96.61% | 100% | 100% | -3.209% | 0%
SECI-III | ERCPL | 300 | 426.3295 | 2021-10-31 | 68872.8453 | 62683.872 | 174.6 | 169.3538 | 204 | 200.6888 | 79.59% | 74.07% | 30.86% | 28.08% | 99.5% | 98.91% | 100% | 100% | -2.876% | -6.585%
SECI-III | ERCPL | 300 | 436.8501 | 2021-11-30 | 61392.2062 | 53646.08 | 135 | 132.217 | 168.9 | 168.0337 | 83.62% | 73.3% | 28.42% | 24.84% | 99.5% | 99.71% | 100% | 100% | -0.5276% | -8.654%
SECI-III | ERCPL | 300 | 444.9055 | 2021-12-31 | 61807.1225 | 51885.6 | 124.1 | 114.5987 | 162.6 | 146.8345 | 85.87% | 79.95% | 27.69% | 23.25% | 99.5% | 99.34% | 100% | 100% | -2.316% | -5.65%
SECI-III | ERCPL | 300 | 445.4393 | 2022-01-31 | 64420.8756 | 57593.376 | 132.8 | 126.5179 | 170.1 | 160.5455 | 85.45% | 81.09% | 28.86% | 25.8% | 99.5% | 99.31% | 100% | 99.9% | -2.847% | -2.17%
SECI-III | ERCPL | 300 | 445.4393 | 2022-02-28 | 63303.9812 | 61555.36 | 144.8 | 150.7646 | 174 | 180.9115 | 82.09% | 76.79% | 31.4% | 30.53% | 99.5% | 99.47% | 100% | 99.63% | -3.131% | -2.483%
SECI-III | ERCPL | 300 | 445.4393 | 2022-03-31 | 75049.1013 | 71367.744 | 194.7 | 201.2519 | 216.1 | 222.3009 | 78.36% | 72.12% | 33.62% | 31.97% | 99.5% | 99.93% | 100% | 100% | -2.901% | -3.03%
SECI-III | ERCPL | 300 | 445.638 | 2022-04-30 | 73220.2639 | 72238.848 | 209.6 | 220.8757 | 215.9 | 227.0443 | 76.48% | 71.49% | 33.9% | 33.44% | 99.5% | 99.87% | 100% | 100% | -3.184% | -2.14%
SECI-III | ERCPL | 300 | 446.413 | 2022-05-31 | 75517.4708 | 72090.208 | 221.5 | 229.8106 | 217.1 | 224.6078 | 78.31% | 71.96% | 33.83% | 32.3% | 99.5% | 99.91% | 100% | 100% | -3.439% | -2.93%
SECI-III | ERCPL | 300 | 446.5031 | 2022-06-30 | 67324.104 | 67445.248 | 198.6 | 213.1332 | 190.5 | 203.2221 | 79.55% | 74.46% | 31.17% | 31.22% | 99.5% | 99.83% | 100% | 100% | -2.537% | -2.04%
SECI-III | ERCPL | 300 | 447.0515 | 2022-07-31 | 61732.76 | 54100.224 | 177 | 162.85 | 171.5 | 157.32 | 80.92% | 77.19% | 27.66% | 24.24% | 99.5% | 99.65% | 100% | 100% | -2.167% | -0.36%
SECI-III | ERCPL | 300 | 447.9628 | 2022-08-31 | 64124.8528 | 53422.944 | 176.4 | 155.0984 | 177.7 | 154.7145 | 80.96% | 77.65% | 28.73% | 23.94% | 99.5% | 99.27% | 100% | 99.92% | -2.507% | -0.46%
SECI-III | ERCPL | 300 | 448.3171 | 2022-09-30 | 68458.6739 | 67125.728 | 181.1 | 188.8552 | 194.4 | 202.4372 | 78.94% | 74.1% | 31.69% | 31.08% | 99.5% | 99.81% | 100% | 100% | -2.865% | -1.56%
SECI-III | ERCPL | 300 | 448.3345 | 2022-10-31 | 72065.4975 | 69307.328 | 174.6 | 175.2819 | 204 | 203.8132 | 79.19% | 76.02% | 32.29% | 31.05% | 99.5% | 99.77% | 100% | 100% | -1.686% | -2.44%
SECI-III | ERCPL | 300 | 448.3467 | 2022-11-30 | 62692.8219 | 60799.008 | 135 | 137.1418 | 168.9 | 171.9937 | 83.21% | 78.9% | 29.02% | 28.15% | 99.5% | 99.93% | 100% | 100% | -1.686% | -2.32%
SECI-III | ERCPL | 300 | 448.3467 | 2022-12-31 | 61973.7454 | 60948.16 | 124.1 | 130.5268 | 162.6 | 171.8058 | 85.44% | 80.18% | 27.77% | 27.31% | 99.5% | 98.68% | 100% | 100% | -3.11% | -2.48%
SECI-III | ERCPL | 300 | 448.3467 | 2023-01-31 | 64517.1458 | 63197.28 | 132.8 | 137.3141 | 170.1 | 174.3934 | 85.02% | 81.51% | 28.91% | 28.31% | 99.5% | 99.16% | 100% | 99.63% | -2.448% | -2.31%
SECI-III | ERCPL | 300 | 448.3467 | 2023-02-28 | 63398.5823 | 59671.04 | 144.8 | 150.4873 | 174 | 180.1725 | 81.68% | 76.25% | 31.45% | 29.6% | 99.5% | 96.88% | 100% | 99.29% | -1.924% | -2.13%
SECI-III | ERCPL | 300 | 448.3467 | 2023-03-31 | 75161.2542 | 67980.672 | 194.7 | 184.0646 | 216.1 | 202.3952 | 77.97% | 75.02% | 33.67% | 30.46% | 99.5% | 99.86% | 100% | 100% | -0.1259% | -1.456%
SECI-III | ERCPL | 300 | 448.3467 | 2023-04-30 | 72929.5305 | 68328.128 | 209.6 | 205.3056 | 215.9 | 209.5863 | 75.72% | 72.82% | 33.76% | 31.63% | 99.5% | 99.85% | 100% | 100% | -0.151% | -2%
SECI-III | ERCPL | 300 | 448.3467 | 2023-05-31 | 75089.195 | 71408.672 | 221.5 | 228.1174 | 217.1 | 220.7134 | 77.53% | 73.45% | 33.64% | 31.99% | 99.5% | 98.25% | 100% | 100% | -1.714% | -1.771%
SECI-III | ERCPL | 300 | 448.3467 | 2023-06-30 | 67263.1714 | 66229.888 | 198.6 | 207.1279 | 190.5 | 196.037 | 79.15% | 76% | 31.14% | 30.66% | 99.5% | 99.15% | 100% | 100% | -3.56% | -1.531%
SECI-III | ERCPL | 300 | 448.3467 | 2023-07-31 | 61601.2288 | 64062.976 | 177 | 195.3266 | 171.5 | 186.7982 | 80.52% | 76.82% | 27.6% | 28.7% | 99.5% | 99.57% | 100% | 100% | -3.461% | -0.6995%
SECI-III | ERCPL | 300 | 448.3467 | 2023-08-31 | 63858.0561 | 65427.904 | 176.4 | 196.4225 | 177.7 | 196.0407 | 80.55% | 74.65% | 28.61% | 29.31% | 99.5% | 99.72% | 100% | 100% | -3.588% | -1.764%
SECI-III | ERCPL | 300 | 448.3467 | 2023-09-30 | 68119.9708 | 63012.256 | 181.1 | 179.3213 | 194.4 | 191.2213 | 78.55% | 73.75% | 31.54% | 29.17% | 99.5% | 99.66% | 100% | 100% | -3.181% | -1.44%
SECI-III | ERCPL | 300 | 448.3467 | 2023-10-31 | 71706.1622 | 64901.76 | 174.6 | 163.7386 | 204 | 191.6879 | 78.79% | 75.9% | 32.13% | 29.08% | 99.5% | 99.49% | 100% | 100% | -2.742% | -1.364%
SECI-III | ERCPL | 300 | 448.3467 | 2023-11-30 | 62378.5313 | 51211.072 | 135 | 116.676 | 168.9 | 144.3449 | 82.79% | 79.22% | 28.88% | 23.71% | 99.5% | 99.89% | 100% | 100% | -0.8003% | -1.431%
SECI-III | ERCPL | 300 | 448.3467 | 2023-12-31 | 61663.0597 | 59413.376 | 124.1 | 124.3882 | 162.6 | 165.7518 | 85.01% | 80.06% | 27.63% | 26.62% | 99.5% | 99.86% | 100% | 100% | -0.058% | -1.748%
SECI-III | ERCPL | 300 | 448.3467 | 2024-01-31 | 64193.7095 | 58941.92 | 132.8 | 127.4055 | 170.1 | 164.2149 | 84.6% | 80.97% | 28.76% | 26.41% | 99.5% | 98.87% | 100% | 100% | -0.08% | -1.62%
SECI-III | ERCPL | 300 | 448.3467 | 2024-02-29 | 63080.7536 | 60460.608 | 144.8 | 145.494 | 174 | 175.2304 | 81.27% | 77.13% | 30.21% | 28.96% | 99.5% | 99.78% | 100% | 100% | -0.1195% | -1.55%
SECI-III | ERCPL | 300 | 448.3467 | 2024-03-31 | 74784.457 | 71643.94 | 194.7 | 194.4917 | 216.1 | 215.8082 | 77.57% | 74.08% | 33.51% | 32.1% | 99.5% | 99.95% | 100% | 100% | -0.0929% | -1.99%
SECI-III | ERCPL | 300 | 448.3467 | 2024-04-30 | 72564.8828 | 65689.28 | 209.6 | 191.2995 | 215.9 | 196.8218 | 75.34% | 74.73% | 33.59% | 30.41% | 99.5% | 99.61% | 100% | 100% | -0.1812% | -1.58%
SECI-III | ERCPL | 300 | 448.3467 | 2024-05-31 | 74713.749 | 72652.704 | 221.5 | 228 | 217.1 | 223.25 | 77.14% | 72.68% | 33.47% | 32.55% | 99.5% | 99.87% | 100% | 100% | -0.2% | -2.25%
SECI-III | ERCPL | 300 | 448.3467 | 2024-06-30 | 66926.8555 | 66712.544 | 198.6 | 208.2414 | 190.5 | 199.1303 | 78.75% | 74.85% | 30.98% | 30.89% | 99.5% | 99.83% | 100% | 100% | -0.5286% | -1.71%
SECI-III | ERCPL | 300 | 448.3467 | 2024-07-31 | 61293.2226 | 65727.552 | 177 | 199.1783 | 171.5 | 194.2427 | 80.11% | 75.99% | 27.46% | 29.45% | 99.5% | 99.32% | 100% | 100% | -0.3315% | -0.79%
SECI-III | ERCPL | 300 | 448.3467 | 2024-08-31 | 63538.7658 | 50124.128 | 176.4 | 145.5852 | 177.7 | 146.4989 | 80.15% | 77.71% | 28.47% | 22.46% | 99.5% | 98.2% | 100% | 100% | -0.2186% | -0.25%
SECI-III | ERCPL | 300 | 448.3467 | 2024-09-30 | 67779.3709 | 63393.888 | 181.1 | 175.7966 | 194.4 | 191.32 | 78.16% | 74.67% | 31.38% | 29.35% | 99.5% | 98.97% | 100% | 100% | -0.1976% | -1.08%
SECI-III | ERCPL | 300 | 448.3467 | 2024-10-31 | 71347.6314 | 64137.792 | 174.6 | 163.23 | 204 | 192.98 | 78.4% | 74.31% | 31.97% | 28.74% | 99.5% | 99.76% | 100% | 100% | -0.491% | -1.08%
SECI-III | ERCPL | 300 | 448.3467 | 2024-11-30 | 62066.6387 | 58676.064 | 135 | 133.2662 | 168.9 | 172.0071 | 82.37% | 76.14% | 28.73% | 27.16% | 99.5% | 99.93% | 100% | 100% | -0.6963% | -2.13%
SECI-III | ERCPL | 300 | 448.3467 | 2024-12-31 | 61354.7444 | 56765.984 | 124.1 | 122.0631 | 162.6 | 162.536 | 84.58% | 78.21% | 27.49% | 25.43% | 99.5% | 99.6% | 100% | 100% | -0.6946% | -2.17%
SECI-III | ERCPL | 300 | 448.3467 | 2025-01-31 | 63872.741 | 61904.06 | 132.8 | 133.16 | 170.1 | 174.86 | 84.17% | 80.04% | 28.62% | 27.73% | 99.5% | 98.65% | 100% | 100% | -0.9524% | -1.95%
SECI-III | ERCPL | 300 | 448.3467 | 2025-02-28 | 62765.3498 | 57634.88 | 144.8 | 137.78 | 174 | 167.29 | 80.86% | 76.98% | 31.13% | 28.59% | 99.5% | 99.82% | 100% | 100% | -1.338% | -1.95%
Formulas:
Months = EOMONTH([Months, row above],1)
Note on Q3: Author: Plant Uptime-97.7127272727273%
Note on Q21: Author: TL Down for 7 Hours considered in PU

## PV Syst Data
Months | Egrid (kWh) with 300 GL, 2% MQ, 100% PA | Actual Gen. | Actual PA | Shortfall in Gen(%) wrt PV syst | Grid Compliance | Shortfall in PA(%) wrt PV syst | Performance
2022-04-01 | 75839.5342 | 72238.848 | 99.87% | -4.748% | -3.184% | -0.1282% | -1.435% | 72331.5941 | -4.625%
2022-05-01 | 77298.7091 | 72090.208 | 99.91% | -6.738% | -3.439% | -0.08531% | -3.213% | 72151.7638 | -6.659%
2022-06-01 | 71660.8265 | 67445.248 | 99.83% | -5.883% | -2.537% | -0.1729% | -3.173% | 67562.0766 | -5.72%
2022-07-01 | 57139.5159 | 54100.224 | 99.65% | -5.319% | -2.167% | -0.35% | -2.802% | 54290.2398 | -4.987%
2022-08-01 | 57853.703 | 53422.944 | 99.27% | -7.659% | -2.507% | -0.7319% | -4.42% | 53816.8515 | -6.978%
2022-09-01 | 71161.1488 | 67125.728 | 99.81% | -5.671% | -2.865% | -0.1871% | -2.618% | 67251.5731 | -5.494%
2022-10-01 | 72387.9927 | 69307.328 | 99.77% | -4.256% | -1.686% | -0.2266% | -2.343% | 69464.7612 | -4.038%
2022-11-01 | 63639.187 | 60799.008 | 99.93% | -4.463% | -1.692% | -0.07241% | -2.699% | 60843.0641 | -4.394%
2022-12-01 | 65662.9329 | 60948.16 | 98.68% | -7.18% | -3.109% | -1.315% | -2.756% | 61760.5089 | -5.943%
2023-01-01 | 65826.6034 | 63197.28 | 99.16% | -3.994% | -2.448% | -0.8372% | -0.7089% | 63730.8184 | -3.184%
2023-02-01 | 64101.2095 | 59671.04 | 96.88% | -6.911% | -1.924% | -3.122% | -1.866% | 61593.7075 | -3.912%
2023-03-01 | 70539.8109 | 67980.672 | 99.86% | -3.628% | -0.1259% | -0.1398% | -3.362% | 68075.8697 | -3.493%
2023-04-01 | 71196.9984 | 68328.128 | 99.85% | -4.029% | -0.151% | -0.1459% | -3.733% | 68427.9565 | -3.889%
2023-05-01 | 75020.0917 | 71408.672 | 98.25% | -4.814% | -1.714% | -1.754% | -1.347% | 72683.2058 | -3.115%
2023-06-01 | 69657.6094 | 66229.888 | 99.15% | -4.921% | -3.56% | -0.8467% | -0.5146% | 66795.4174 | -4.109%
2023-07-01 | 67031.2173 | 64062.976 | 99.57% | -4.428% | -3.461% | -0.4268% | -0.5407% | 64337.5932 | -4.018%
2023-08-01 | 69685.3798 | 65427.904 | 99.72% | -6.11% | -3.588% | -0.2759% | -2.245% | 65608.9392 | -5.85%
2023-09-01 | 67083.9659 | 63012.256 | 99.66% | -6.07% | -3.181% | -0.3408% | -2.547% | 63227.7605 | -5.748%
2023-10-01 | 66655.0027 | 64901.76 | 99.49% | -2.63% | -2.742% | -0.5078% | 0.6191% | 65232.9935 | -2.133%
2023-11-01 | 52731.6941 | 51211.072 | 99.89% | -2.884% | -0.8003% | -0.1071% | -1.976% | 51265.9607 | -2.78%
2023-12-01 | 60867.0368 | 59413.376 | 99.86% | -2.388% | -0.058% | -0.1427% | -2.188% | 59498.2745 | -2.249%
2024-01-01 | 60236.5142 | 58941.92 | 98.87% | -2.149% | -0.08164% | -1.13% | -0.9372% | 59615.7551 | -1.031%
2024-02-01 | 60986.5283 | 60460.608 | 99.78% | -0.8624% | -0.1195% | -0.2227% | -0.5201% | 60595.571 | -0.6411%
2024-03-01 | 73308.703 | 71643.94 | 99.95% | -2.271% | -0.0929% | -0.04556% | -2.132% | 71676.5936 | -2.226%

## EPC (hidden)
| SECI-III | [7 empty] | AC Cap |  |  | 300 | DC Cap |  |  |  | SECI-III -Shortfall Analysis
Connected DC Capacity (MWp) | Months | Budget Gen (MWHr) | Actual Gen (MWHr) | Budget GHI (KWHr/m2) | Actual GHI (KWHr/m2) | Budget GTI (KWHr/m2) | Actual GTI (KWHr/m2) | PR Budgeted(%) | PR Achieved(%) | CUF Budgeted (%) | CUF Achieved (%) | Budgeted Plant Av(%) | Actual Plant Av(%) | Budgeted Grid Av(%) | Actual Grid Av(%) |  | Months | Shortfall in Gen(%) wrt Budget | Shortfall in Rad(%) | Shortfall in Plant Av(%) | Shortfall in Grid Av(%) | Generation loss in Grid Compliance (%) | Soil Loss(%)
309.2589 | 2021-08-31 | 25319.4141 | 26127.968 | 96.7355 | 114.724 | 97.4484 | 117.2813 | 84.86% | 74.13% | 20.69% | 21.35% | 99% | 97.17% | 100% | 99.45% | -17.16% | 2021-08-31 | 3.193% | 20.35% | -1.827% | -0.5526% | -1.45%
407.1342 | 2021-09-30 | 61237.4411 | 50430.016 | 181.1 | 160.6876 | 194.4 | 171.885 | 78.15% | 74.59% | 28.35% | 23.35% | 99% | 96.61% | 100% | 100% | -6.067% | 2021-09-30 | -17.65% | -11.58% | -2.389% | 0% | -3.209%
426.3295 | 2021-10-31 | 67500.5538 | 62683.872 | 174.6 | 169.3538 | 204 | 200.6888 | 78.4% | 74.07% | 30.24% | 28.08% | 99% | 98.91% | 100% | 100% | -5.513% | 2021-10-31 | -7.136% | -1.623% | -0.08509% | 0% | -2.876% | -6.585%
436.8501 | 2021-11-30 | 60168.9665 | 53646.08 | 135 | 132.217 | 168.9 | 168.0337 | 82.37% | 73.3% | 27.86% | 24.84% | 99% | 99.71% | 100% | 100% | -10.33% | 2021-11-30 | -10.84% | -0.5129% | 0.7062% | 0% | -0.5276% | -8.654%
444.9055 | 2021-12-31 | 60575.6156 | 51885.6 | 124.1 | 114.5987 | 162.6 | 146.8345 | 84.58% | 79.95% | 27.14% | 23.25% | 99% | 99.34% | 100% | 100% | -4.65% | 2021-12-31 | -14.35% | -9.696% | 0.3409% | 0% | -2.316% | -5.65%
445.4393 | 2022-01-31 | 63137.2897 | 57593.376 | 132.8 | 126.5179 | 170.1 | 160.5455 | 84.17% | 81.09% | 28.29% | 25.8% | 99% | 99.31% | 100% | 99.9% | -3.164% | 2022-01-31 | -8.781% | -5.617% | 0.3108% | -0.09692% | -2.847% | -2.17%
445.4393 | 2022-02-28 | 62042.6494 | 61555.36 | 144.8 | 150.7646 | 174 | 180.9115 | 80.86% | 76.79% | 30.78% | 30.53% | 99% | 99.47% | 100% | 99.63% | -4.758% | 2022-02-28 | -0.7854% | 3.972% | 0.4735% | -0.3736% | -3.131% | -2.483%
445.4393 | 2022-03-31 | 73553.7479 | 71367.744 | 194.7 | 201.2519 | 216.1 | 222.3009 | 77.18% | 72.12% | 32.95% | 31.97% | 99% | 99.93% | 100% | 100% | -5.841% | 2022-03-31 | -2.972% | 2.869% | 0.929% | 0% | -2.901% | -3.03%
445.638 | 2022-04-30 | 71761.3501 | 72238.848 | 209.6 | 220.8757 | 215.9 | 227.0443 | 75.34% | 71.49% | 33.22% | 33.44% | 99% | 99.87% | 100% | 100% | -4.496% | 2022-04-30 | 0.6654% | 5.162% | 0.8718% | 0% | -3.184% | -2.14%
446.413 | 2022-05-31 | 74012.7851 | 72090.208 | 221.5 | 229.8106 | 217.1 | 224.6078 | 77.14% | 71.96% | 33.16% | 32.3% | 99% | 99.91% | 100% | 100% | -6.056% | 2022-05-31 | -2.598% | 3.458% | 0.9147% | 0% | -3.439% | -2.93%
446.5031 | 2022-06-30 | 65982.6712 | 67445.248 | 198.6 | 213.1332 | 190.5 | 203.2221 | 78.36% | 74.46% | 30.55% | 31.22% | 99% | 99.83% | 100% | 100% | -4.462% | 2022-06-30 | 2.217% | 6.678% | 0.8271% | 0% | -2.537% | -2.04%
447.0515 | 2022-07-31 | 60502.7348 | 54100.224 | 177 | 162.85 | 171.5 | 157.32 | 79.71% | 77.06% | 28.01% | 25.05% | 99% | 99.83% | 100% | 100% | -2.314% | 2022-07-31 | -10.58% | -8.268% | 0.8271% | 0% | -2.167% | -0.36%
447.9628 | 2022-08-31 | 62847.1652 | 53422.944 | 176.4 | 155.0984 | 177.7 | 154.7145 | 79.75% | 77.22% | 29.1% | 24.73% | 99% | 99.83% | 100% | 100% | -2.06% | 2022-08-31 | -15% | -12.93% | 0.8271% | 0% | -2.507% | -0.46%
448.3171 | 2022-09-30 | 67094.6348 | 67125.728 | 181.1 | 188.8552 | 194.4 | 202.4372 | 77.76% | 74.09% | 31.06% | 31.08% | 99% | 99.83% | 100% | 100% | -4.088% | 2022-09-30 | 0.04634% | 4.134% | 0.8271% | 0% | -2.865% | -1.56%
| YTD FY-21-22 | 473535.6781 | 435290.016 | 1183.8355 | 1170.1156 | 1387.5484 | 1368.4812 | 81.32% | 75.76% | 28.29% | 26.15% | 99% | 98.81% | 100% | 99.87% | -6.702% | YTD FY-21-22 | -8.077% | -1.374% | -0.1927% | -0.1279% | -2.668% | -4.762%
| YTD FY-22-23 | 335106.7064 | 319297.472 | 983.1 | 981.768 | 972.7 | 966.9088 | 78.06% | 74.44% | 30.81% | 29.35% | 99% | 99.85% | 100% | 100% | -4.122% | YTD FY-22-23 | -4.718% | -0.5954% | 0.8535% | 0% | -2.767% | -1.586%
Note on N4: Author: Plant Uptime-97.7127272727273%
Note on D16: Author: Standby Based Value will be updated once DSM published

## Sheet2 (hidden)
|  | PV Syst Lenders | PV Syst SNW | 2021-08-15
| AC LOADING | 300 MW | 300 MW | 300 MW
| Variants | Fixed Tilt | Fixed Tilt | Fixed Tilt
| Pitch (m) | 7.5 | 7.5 | 7.5
| Type of support | Fixed 2x58 portrait | Fixed 2x58 portrait | Fixed 2x58 portrait
| Tilt | 18° | 18° | 18°
| Module type | JKM 400M-72H-V & JKM 405M-72H-V | JKM 400M-72H-V & JKM 405M-72H-V
| Power [Wc] | 400 Wp & 405 Wp | 400 Wp & 405 Wp | 400 Wp & 405 Wp
| Make | Jinko solar | Jinko solar | Jinko solar
| Inverter | SG3125HV-20 | SG3125HV-20 | SG3125HV-20
| Ratio DC/AC | 1.5 | 1.5 | 1.3573
| Watt peak power for simulation (MWp) | 450.001 | 450.001 | 450.001
| PV plant AC power (MW) | 300 | 300 | 300
| PV plant DC Capacity (MWp) | 450.001 | 450.001 | 407.18
| No. of Modules | 1115137 | 1115137 | 1009120.1983
| Total Area | 2243673 | 2243673 | 2030365.5449
| Per Module Area | 2.012 | 2.012 | 2.012
Energy available in plane of collectors From front | Hgh [kWh/m²/an] | 2070.1 | 2070.1
| Transposition Factor | 9.449% | 9.449%
| Hginc [kWh/m²/an] | 2265.7 | 2265.7 | 114.724
| Global incident below threshold | -0.026% | -0.026% | -0.026%
| Shading losses | -1.59% | -1.59% | -1.59%
| IAM losses | -1.356% | -1.356% | -1.356%
| Soiling losses | -2% | -2% | -2%
| Ground reflection on front side | 0% | 0% | 0%
| Gain fro rear END | 0% | 0% | 0%
| Bifacilaity Factor | 0% | 0% | 0%
| Effective irradiation from rear side | 0% | 0% | 0%
| Hginc eff [kWh/m²/an] | 2154.8917 | 2154.8917 | 109.1132
Energy available at inverter output | E_brutto [kWh/kWp/an] | 976644.2255 | 976644.2255 | 44751.0197
| Total system losses | -15.88% | -15.88% | -15.88%
| Module Degradation | 0% | 0% | 0%
| Irradiance losses | 0.12% | 0.12% | 0.12%
| Temperature losses | -7.951% | -7.951% | -7.951%
| Shading losses (electrical) | -0.033% | -0.033% | -0.033%
| Module quality losses | 0.8% | 0.8% | 0.8%
| LID losses | -1.9% | -1.9% | -1.9%
| Mismatch losses | -0.6% | -0.6% | -0.6%
| Mismatch due to Rear side | 0% | 0% | 0%
| DC ohmic losses | -1.12% | -1.12% | -1.12%
| Inverter efficiency losses | -1.367% | -1.367% | -1.367%
| Inv loss over nom inv power | -4.75% | -4.75% | -4.75%
| Inv loss due to voltage threshold | -0.006% | -0.006% | -0.006%
| Night consumption | 0% | 0% | 0%
| E_netto inverter [kWh/kWp/an] | 821520.7017 | 821520.7017 | 37643.0722
Energy available at Grid input metering | AC cabling losses (Inv to Trafo) |  | -0.336% | -0.336%
| Auxiliaries losses |  | -0.397% | -0.397%
| Transformer losses |  | -1.377% | -1.377%
| Transformer (33kV/220kV) losses |  | 0% | 0%
| Transmission Losses |  | 0% | 0%
| Transmission Losses (33+220kV) |  | 0% | 0%
| Plant availability and switchyard |  | 0% | 1%
| Grid Limitation |  | 0% | 0%
| E_netto AC COD [kWh/kWp/an] |  | 804280.3418 | 37221.6291
| PR COD |  | 78.88% | 79.68%
| Degradation 2nd year |  | -0.5% | -0.5%
| E_netto AC year 2 [kWh/kWp/an] |  | 800258.9401 | 37035.5209
| PR year 2 |  | 35321% | 32282%
| E_nette AC year 10 [kWh/kWp/an] |  | 764247.2878 | 35368.9225
| PR year 10 |  | 33731% | 30830%
| E_nette AC year 25 [kWh/kWp/an] |  | 704227.8673 | 32591.2584
| PR year 25 |  | 31082% | 28408%
| Average net production AC [kWh/kWp/an] |  | 752243.4037 | 34813.3897
| PR average |  | 33201% | 30345%
| Yearly net production (year 1) [GWh/year] |  | 804280.3418 | 37221.6291
| Yearly net production (year 2) [GWh/year] |  | 360.1173 | 15.0801
| CUF year 1 |  | 30.6% | 517%
| Yearly net production (year 10) [GWh/year] |  | 343.912 | 14.4015
| CUF year 10 |  | 13086% | 548%
| Yearly net production (year 25) [GWh/year] |  | 316.9032 | 13.2705
| CUF year 25 |  | 12059% | 505%
| CUF year 2 |  | 13703% | 573.8%
| P50 1st year |  | 804280.3418 | 37221.6291
P50 averaged on 25 years
P75 1st year
P75 averaged on 25 years
P90 1st year
P90 averaged on 25 years
P99 1st year
P99 averaged on 25 years
Uncertainity 1 year
Uncertainity 25 years
| P50 2nd year |  | 800258.9401 | 37035.5209
1787.2896
|  |  | 1787.2857 | 1005.0848
-23.89%